## Cover
Flex BSC Modbus Map
JF1 Rack
LGES, Ltd. / Research Park
CTO.BMS Research & Development
SW Development Team 4
Copyright © 2024 LGES, Ltd. All Rights Reserved.
Though every care has been taken to ensure the accuracy of this document, LGES, Ltd. cannot accept responsibility for any errors or omissions or for any loss occurred to any person, whether legal or natural, from acting, or refraining from action, as a result of the information contained herein. Information in this document is subject to change at any time without obligation to notify any person of such changes. LGES, Ltd. may have patents or patent pending applications, trademarks copyrights or other intellectual property rights covering subject matter in this document. The furnishing of this document does not give the recipient or reader any license to these patents, trademarks copyrights or other intellectual property rights. No part of this document may be communicated, distributed, reproduced or transmitted in any form or by any means, electronic or mechanical or otherwise, for any purpose, without the prior written permission of LGES Co, Ltd. The document is subject to revision without further notice. All brand names and product names mentioned in this document are trademarks or registered trademarks of their respective owners.

## Description
Document Information
Document Number | - |  |  |  | Document Name | Flex BSC Modbus Map
Company | LGES, Ltd. / Research Park |  |  | Category | Category | Communication Database
Division | ESS.Development.ESS BMS Dev |  |  | Confidentiality | Target Model | JF1 Rack
Part | SW Development Team 2 |  |  | Date | Applying Point
Confidentiality | Confidential |  |  | Date | Date
Documentation Approval
Author |  |  | Reviewer |  |  | Approver
Paek SeungKyu Lee Chungyong |  |  | Hyeon Byenggyu |  |  | Lee SeongKeun
Revision History
Version | Date | Comments |  |  | Author | Position | Approval
AA | 2023-02-15 | First Release |  |  | Paek SeungKyu | BSC Engineer
AB | 2023-12-08 | Add JF1 |  |  | Hyeon Byenggyu Lee Chungyong | BSC Engineer
AC | 2023-07-17 | Removed FullChargeMode |  |  | Hyeon Byenggyu | BSC Engineer
Changed G3L_RBMS_Modbus_Map_v1.8
AE | 2024-12-17 | Changed G3L_RBMS_Modbus_Map_v2.2 |  |  | Hyeon Byenggyu Lee Chungyong | BSC Engineer
Added Non-balancing entry period (Rack Data)
Added PreVPC status (BSC Data)
| 2025-01-03 | The names of some diagnoses have changed.
AF | 2025-07-30 | Added Reset Command (C2B). Updated request ack.table. |  |  | Paek SeungKyu | BSC Engineer
Updated request ack.table.
Modified the address range for disabled racks in the Start command within C2B.
Updated the description of BSC SOC value (B2C)
Added BSC warning condition to BSC Fault ack.
Added SOC condition to Over Voltage Deviation ack.
Applied G3L_RBMS_Modbus_Map_v2.5d

## Common
Encoding Rule |  |  |  |  | Data legend
Register Size(bit) | Value Type | Value | Encoded Value |  | Value | Description
16 | SINT | 32767 | 0x7FFF |  | Reserved | Reserved for future use
16 | SINT | -32768 | 0x8000 |  | Removed | No longer used
16 | UINT | 65535 | 0xFFFF |  | N/A | Not used
Binary Encoding Rule
| Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
Byte0 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0
Byte1 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8
[Input Register - Slave ID 1] : BSC → Controller (B2C) |  |  |  |  | [Holding Register Slave ID 1 ] : Controller → BSC (C2B)
BSC Data |  |  |  |  | Controller Data
Source | Start | End | Function Code |  | Source | Start | End | Function Code
Nameplate | 30000 | 30029 | Read : 0x04 |  | Controller | 40000 | 40200 | Write: 0x06, 0x10
Request Ack. | 30030 | 30034
Essential | 30035 | 30069
Summary | 30070 | 30169
Rack Periodic Data
Source | Start | End | Function Code
Rack1 Nameplate | 30170 | 30219 | Read : 0x04
Rack1 Summary | 30220 | 30319
Rack2 Nameplate | 30320 | 30369
Rack2 Summary | 30370 | 30469
… Rack N | … 30170 + (N-1) * 150 | … Start(N) + 150 - 1
Rack79 | 41870 | 42019
Rack80 | 42020 | 42169
BSC Flag Data
Source | Start | End | Function Code
Disabled Rack | 1 | N | Read : 0x02
Online Rack | N + 1 | 2N
Alarm Rack | 2N + 1 | 3N
Waring Rack | 3N +1 | 4N
Fault Rack | 4N + 1 | 5N
Non-balancing Rack | 5N + 1 | 6N

## B2C(BSC Data)
Input Registers(Modbus-TCP) Slave ID 1
The Controller must use the function code 4(0x04) to read the data.
Battery Section Controller(BSC) Data
Updated every 1 second, Read every 1 second.(except Nameplate)
Source | MODBUS Address | Address Hex | Type | Name | Value | Unit | Scale | Description
Nameplate (Fixed) | 30000 | 7530 | uint32 | BSC S/W Version | b0 ~ b31 : Version(x.x.x.x) | - | - | BSC SW Version e.g.) 0x0102(30000), 0x1112(30001) → Ver 1.2.17.18
| 30001 | 7531 |  |  |  | - | -
| 30002 | 7532 |  | Reserved |  | - | -
| 30003 | 7533 |  | Reserved |  | - | -
| 30004 | 7534 |  | Reserved |  | - | -
| 30005 | 7535 | uint16 | No. of total racks | b0 ~ b15: The number of total racks | ea | - | The number of total racks in the battery section e.g.) 0x000B → 11ea
| 30006 | 7536 |  | Reserved |  | - | -
| 30007 | 7537 |  | Reserved |  | - | -
| 30008 | 7538 |  | Reserved |  | - | -
| 30009 | 7539 |  | Reserved |  | - | -
| 30010 | 753A |  | Removed |  | - | -
| 30011 | 753B |  | Reserved |  | - | -
| 30012 | 753C |  | Reserved |  | - | -
| 30013 | 753D |  | Reserved |  | - | -
| 30014 | 753E |  | Reserved |  | - | -
| 30015 | 753F |  | Reserved |  | - | -
| 30016 | 7540 |  | Reserved |  | - | -
| 30017 | 7541 |  | Reserved |  | - | -
| 30018 | 7542 |  | Reserved |  | - | -
| 30019 | 7543 |  | Reserved |  | - | -
| 30020 | 7544 |  | Reserved |  | - | -
| 30021 | 7545 |  | Reserved |  | - | -
| 30022 | 7546 |  | Reserved |  | - | -
| 30023 | 7547 |  | Reserved |  | - | -
| 30024 | 7548 |  | Reserved |  | - | -
| 30025 | 7549 |  | Reserved |  | - | -
| 30026 | 754A |  | Reserved |  | - | -
| 30027 | 754B |  | Reserved |  | - | -
| 30028 | 754C |  | Reserved |  | - | -
| 30029 | 754D |  | Reserved |  | - | -
Request Ack. | 30030 | 754E | uint16 | Request Acknowledge | 0x0000: None | enum | - | Initial status
[5 empty] | 0x0001: In Progress |  |  | The request was accepted and it is now in progress
[5 empty] | 0x0002: Done |  |  | The process of the request has done - This will change to 0x0 None after 3seconds if there isn't command request anymore.
[5 empty] | 0x0003: Reserved |  |  | Reserved
[5 empty] | 0x0004: Reserved |  |  | Reserved
[5 empty] | 0x0005: BMS Not Connected |  |  | Not Accepted: The BSC isn’t communicating with the racks yet.
[5 empty] | 0x0006: BMS Already Connected |  |  | Not Accepted: The BSC has already been communicating with the racks.
[5 empty] | 0x0007: Under BSC Initializing |  |  | Not Accepted: The BSC is initializing the communication with the racks.
[5 empty] | 0x0008: All Contactors Already Opened |  |  | Not Accepted: Every rack’s contactor is already opened.
[5 empty] | 0x0009: BSC Already Online |  |  | Not Accepted: There is(are) one or more online racks.
[5 empty] | 0x000A: Current Flows |  |  | Not Accepted: The current is now flowing into or out of the battery. (over ±0.5A * the number of online racks)
[5 empty] | 0x000B: BSC Manual mode |  |  | Not Accepted: BSC state is manual mode.
[5 empty] | 0x000C: BSC Emergency mode |  |  | Not Accepted: BSC state is emergency mode.
[5 empty] | 0x000D : BSC Normal Power Saving mode |  |  | Not Accepted: BSC state is normal power saving mode.
[5 empty] | 0x000E : BSC Normal mode |  |  | Not Accepted: BSC state is normal mode.
[5 empty] | 0x000F: BSC Warning or Fault |  |  | Not Accepted: A warning/fault diagnisos is occurred in the BSC.
[5 empty] | 0x0010: Under Contactor control |  |  | Not Accepted: The BSC is controlling the contactor.
[5 empty] | 0x0011: Over Voltage(or SOC) Deviation |  |  | Not Accepted: Voltage(or SOC) deviation between racks is too high to close.
[5 empty] | 0x0012: Within Cooldown Time |  |  | Not Accepted: Event Clear request is not allowed within cooldown time.
[5 empty] | 0x0013: Target Rack Not Exist |  |  | Not Accepted: There are no target racks.
[5 empty] | 0x0014: removed |  |  | remvoed
[5 empty] | Reserved |  |  | Reserved
[5 empty] | 0x0030: Invalid Request |  |  | Not Accepted: Request is not acceptable. e.g.) when a cotrlloer sends an undefined request to BSC
[5 empty] | 0x0031 : Invalid Argument |  |  | Not Accepted : Invalid Arguments e.g.) when a controller sends request to BSC with invalid arguments
[5 empty] | ~ Undefined |  |  | Reserved
| 30031 | 754F | uint16 | Last Accepted Reqeust | Accepted Controller's Command Request | - | - | Accepted request(Conroller → BSC 40010) will be written while the request ack.(30030) is In Progress(0x0001) or Done(0x0002) If the request is not accepted or turn to None (in 30030), this value will be zero.
| 30032 | 7550 | uint15 | Reserved | Reserved | - | - | Reserved
| 30033 | 7551 | uint16 | Reserved | Reserved | - | - | Reserved
| 30034 | 7552 | uint16 | Reserved | Reserved | - | - | Reserved
Essential | 30035 | 7553 | uint16 | BSC Heartbeat | b0 ~ b15: Heartbeat | - | - | The value of this continually cycles from 0(zero) to 65535 with an interval of 1second.
| 30036 | 7554 | uint16 | BSC State | 0x0000: None | enum | - | Read the BSC operation manual for more information.
[5 empty] | 0x0001: Not Initialized |  | - | ＊Not Initialized: The battery system is shutdown (The BSC isn't communicating with any BMS.)
[5 empty] | 0x0002: Initializing |  | - | ＊Initializing: The BSC and RBMS are being initialized
[5 empty] | 0x0003: Normal |  | - | ＊Normal: The battery system can be operated by controller
[5 empty] | 0x0004: NPS (Normal Power Saving) |  | - | ＊NPS: The battery system makes whole battery packs go into hibernation to save the battery consumption when idle for a long time
[5 empty] | 0x0005: Manual |  | - | ＊Manual: The battery system can be charged or discharged selectively for the maintenance
[5 empty] | 0x0006: Emergency |  | - | ＊Emergency: The battery system or the controller is in emergency (whole racks will be tripped immediately)
[5 empty] | 0x0007: removed |  | - | removed
[5 empty] | : Reserved |  | -
| 30037 | 7555 | bit16 | BSC Information | b0: BSC Alarm | Bit Flags | - | 0: Normal, 1: The BSC alarm has occurred.
[5 empty] | b1: BSC Warning |  | - | 0: Normal, 1: The BSC warning has occurred.
[5 empty] | b2: BSC Fault |  | - | 0: Normal, 1: The BSC fault has occurred.
[5 empty] | b3: Reserved |  |  | Reserved
[5 empty] | b4 ~ b5: BSC Charge status (b00: None, b01: Charge, b10: Dischage, b11: Idle) |  | - | The battery section is charged, discharged or the idle state. * 0b01, Charge : The BSC currents > 0.5A * the number of online racks. * 0b10, Discharge : The BSC currents < -0.5A * the number of online racks. * 0b11, Idle : The BSC is neither charged nor discharged.
[5 empty] | b6: Reserved |  | - | Reserved
[5 empty] | b7: Reserved |  | - | Reserved
[5 empty] | b8: Reserved |  | - | Reserved
[5 empty] | b9: Reserved |  | - | Reserved
[5 empty] | b10: PreVPC |  | - | 0: Not applied, 1: Applied Pre Voltage-based Power Control : System Power Limit is reduced.
[5 empty] | b11: VPC |  | - | 0: Not applied, 1: Applied Voltage-based Power Control : System Power Limit is reduced.
[5 empty] | b12: SPC |  | - | 0: Not applied, 1: Applied SOC-based Power Control : System Power Limit is reduced.
[5 empty] | b13: TPC |  | - | 0: Not applied, 1: Applied Temperature-based Power Control : System Power Limit is reduced.
[5 empty] | b14: Reserved |  | - | Reserved
[5 empty] | b15: Reserved |  | - | Reserved
| 30038 | 7556 | uint16 | No. of online racks | b0 ~ b15: The number of online racks | ea | - | The number of racks which can be charged or discharged e.g.) 0x000B → 11ea
| 30039 | 7557 | uint16 | Reserved | Reserved | - | - | Reserved
| 30040 | 7558 | uint16 | Reserved | Reserved | - | - | Reserved
| 30041 | 7559 | uint16 | Reserved | Reserved | - | - | Reserved
| 30042 | 755A | uint16 | Reserved | Reserved | - | - | Reserved
| 30043 | 755B | uint16 | Controller ↔ BSC LOC | b0: Alarm | Bit Flags | - | There is loss of comm. between Controller and BSC
b1: Warning
b2: Fault
|  |  |  | Reserved | b3: Alarm |  |  | Reserved
b4: Warning
b5: Fault
|  |  |  | Under SOC | b6: Alarm |  |  | Battery SOC reached the lower limit
b7: Warning
b8: Fault
|  |  |  | Over SOC | b9: Alarm |  |  | Battery SOC reached the upper limit
b10: Warning
b11: Fault
|  |  |  | Over Discharge Power | b12: Alarm |  |  | Higher power than the permissible limit has been discharged
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved
| 30044 | 755C | bit16 | Over Charge Power | b0: Alarm | Bit Flags | - | Higher power than the permissible limit has been charged
b1: Warning
b2: Fault
|  |  |  | Removed | b3: Alarm
b4: Warning
b5: Fault
|  |  |  | Removed | b6: Alarm
b7: Warning
b8: Fault
|  |  |  | Reserved | b9: Alarm
b10: Warning
b11: Fault
|  |  |  | Removed | b12: Alarm
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved
| 30045 | 755D | bit16 | Removed | b0: Alarm | Bit Flags | -
b1: Warning
b2: Fault
|  |  |  | Removed | b3: Alarm
b4: Warning
b5: Fault
|  |  |  | SLF (System Logging Failure) | b6: Alarm |  |  | System Logging failed due to lack of HDD space or hardware issues
b7: Warning
b8: Fault
|  |  |  | Reserved | b9: Alarm |  |  | Reserved
b10: Warning
b11: Fault
|  |  |  | Removed | b12: Alarm
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved |  |  | Reserved
| 30046 | 755E | bit16 | Reserved | b0: Alarm | Bit Flags | - | Reserved
b1: Warning
b2: Fault
|  |  |  | Reserved | b3: Alarm |  |  | Reserved
b4: Warning
b5: Fault
|  |  |  | Reserved | b6: Alarm |  |  | Reserved
b7: Warning
b8: Fault
|  |  |  | Removed | b9: Alarm
b10: Warning
b11: Fault
|  |  |  | Removed | b12: Alarm
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved |  |  | Reserved
| 30047 | 755F | bit16 | Removed | b0: Alarm | Bit Flags | -
b1: Warning
b2: Fault
|  |  |  | MFRD | b3: Alarm |  |  | There is a rack that multiple diagnostics have occurred
b4: Warning
b5: Fault
|  |  |  | Removed | b6: Alarm
b7: Warning
b8: Fault
|  |  |  | Over Offline Rack | b9: Alarm
b10: Warning
b11: Fault
|  |  |  | Removed | b12: Alarm
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved |  |  | Reserved
| 30048 | 7560 | bit16 | RBMS SW Version Mismatch | b0: Alarm | Bit Flags | - | If any RACK is not supported, or if there is a different version between racks
b1: Warning
b2: Fault
|  |  |  | N/A | b3: Alarm
b4: Warning
b5: Fault
|  |  |  | N/A | b6: Alarm
b7: Warning
b8: Fault
|  |  |  | N/A | b9: Alarm
b10: Warning
b11: Fault
|  |  |  | Reserved | b12: Alarm |  |  | Reserved
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved |  |  | Reserved
| 30049 | 7561 | bit16 | Reserved | b0: Alarm | Bit Flags | - | Reserved
b1: Warning
b2: Fault
|  |  |  | N/A | b3: Alarm
b4: Warning
b5: Fault
|  |  |  | N/A | b6: Alarm
b7: Warning
b8: Fault
|  |  |  | Reserved | b9: Alarm |  |  | Reserved
b10: Warning
b11: Fault
|  |  |  | Reserved | b12: Alarm |  |  | Reserved
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved |  |  | Reserved
| 30050 | 7562 | bit16 | Reserved | b0: Alarm | Bit Flags | - | Reserved
b1: Warning
b2: Fault
|  |  |  | Reserved | b3: Alarm |  |  | Reserved
b4: Warning
b5: Fault
|  |  |  | Reserved | b6: Alarm |  |  | Reserved
b7: Warning
b8: Fault
|  |  |  | Reserved | b9: Alarm |  |  | Reserved
b10: Warning
b11: Fault
|  |  |  | Reserved | b12: Alarm |  |  | Reserved
b13: Warning
b14: Fault
|  |  |  | Reserved | b15: reserved |  |  | Reserved
| 30051 | 7563 | uint16 | Reserved | Reserved | - | - | Reserved
| 30052 | 7564 | uint16 | Reserved | Reserved | - | - | Reserved
| 30053 | 7565 | uint16 | Reserved | Reserved | - | - | Reserved
| 30054 | 7566 | uint16 | Reserved | Reserved | - | - | Reserved
| 30055 | 7567 | uint16 | BSC SOC (among online racks) | b0 ~ b15: System SOC calculated based on online racks | % | 0.01 | System SOC calculated based on online racks e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30056 | 7568 | uint16 | BSC SOH (among online racks) | b0 ~ b15: Average SOH of all the online racks | % | 0.01 | The average SOH of all the online racks e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30057 | 7569 | uint32 | Anticipated BSC DC Voltage (when there is no online rack) | b0 ~ b31: Anticipated Average voltage of all the battery racks | V | 0.0001 | The anticipated BSC DC voltage, after racks’ contactors are closed e.g.) 0x0072 C14D → 7520589 * 0.0001 = 752.0589V
| 30058 | 756A | [5 empty] | This is valid only when every rack’s contactor is opened. (The number of online racks is zero.)
| 30059 | 756B | uint32 | BSC DC Voltage (among online racks) | b0 ~ b31: Average voltage of all the online racks | V | 0.0001 | The average of voltage of all the online racks
| 30060 | 756C | [5 empty] | e.g.) 0x0072 C14D → 7520589 * 0.0001 = 752.0589V
| 30061 | 756D | sint32 | BSC DC Current | b0 ~ b31: Total amount of DC current in the battery section | A | 0.001 | Total amount of DC current in the battery section
| 30062 | 756E | [5 empty] | e.g.) 0x0001 32A1 → 78497 * 0.001 = 78.497A, 0xFFFE CD5F → -78497 * 0.001 = -78.497A
| 30063 | 756F | uint32 | BSC DC Charge Power Limit | b0 ~ b31: Available Charge Instantaneous Power | kW | 0.001 | The maximum power allowed to charge the battery section e.g.) 0x0001 1BC1 → 72641 * 0.001 = 72.641kW
| 30064 | 7570 | [5 empty] | * The charge power must be kept below the charge power limit within 5seconds. Otherwise, the charge power limit waring or fault will occur following the diagnostic standard.
| 30065 | 7571 | uint32 | BSC DC Discharge Power Limit | b0 ~ b31: Available Discharge Instantaneous Power | kW | 0.001 | The maximum power allowed to discharge the battery section e.g.) 0x0001 1BC1 → 72641 * 0.001 = 72.641kW
| 30066 | 7572 | [5 empty] | * The discharge power must be kept below the discharge power limit within 5seconds. Otherwise, the discharge power limit waring or fault will occur following the diagnostic standard.
| 30067 | 7573 | uint16 | Reserved | Reserved | - | - | Reserved
| 30068 | 7574 | uint16 | Reserved | Reserved | - | - | Reserved
| 30069 | 7575 | uint16 | Reserved | Reserved | - | - | Reserved
Summary | The items below are statistical data summarizing information for all racks. If you would like to read more detailed rack information, please refer to the B2C (Rack Data) sheet.
| 30070 | 7576 | uint16 | N/A |  | - | -
| 30071 | 7577 | uint16 | N/A |  | - | -
| 30072 | 7578 | uint16 | N/A |  | - | -
| 30073 | 7579 | uint16 | N/A |  | - | -
| 30074 | 757A | uint16 | N/A |  | - | -
| 30075 | 757B | uint16 | N/A |  | - | -
| 30076 | 757C | uint16 | N/A |  | - | -
| 30077 | 757D | uint16 | N/A |  | - | -
| 30078 | 757E | uint16 | N/A |  | - | -
| 30079 | 757F | uint16 | N/A |  | - | -
| 30080 | 7580 | uint16 | N/A |  | - | -
| 30081 | 7581 | uint16 | N/A |  | - | -
| 30082 | 7582 | uint16 | N/A |  | - | -
| 30083 | 7583 | uint16 | N/A |  | - | -
| 30084 | 7584 | uint16 | N/A |  | - | -
| 30085 | 7585 | uint16 | N/A |  | - | -
| 30086 | 7586 | uint16 | N/A |  | - | -
| 30087 | 7587 | uint16 | N/A |  | - | -
| 30088 | 7588 | uint16 | N/A |  | - | -
| 30089 | 7589 | uint16 | N/A |  | - | -
| 30090 | 758A | uint16 | N/A |  | - | -
| 30091 | 758B | uint16 | N/A |  | - | -
| 30092 | 758C | uint16 | N/A |  | - | -
| 30093 | 758D | uint16 | N/A |  | - | -
| 30094 | 758E | uint16 | N/A |  | - | -
| 30095 | 758F | uint16 | N/A |  | - | -
| 30096 | 7590 | uint16 | N/A |  | - | -
| 30097 | 7591 | uint16 | N/A |  | - | -
| 30098 | 7592 | uint16 | N/A |  | - | -
| 30099 | 7593 | uint16 | N/A |  | - | -
| 30100 | 7594 | uint16 | Max SOC (among online racks) | b0 ~ b15: Max SOC | % | 0.01 | The highest SOC (among online racks) e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30101 | 7595 | uint16 | Average SOC (among online racks) | b0 ~ b15: Average SOC | % | 0.01 | The average (among online racks) e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30102 | 7596 | uint16 | Min SOC (among online racks) | b0 ~ b15: Min SOC | % | 0.01 | The lowest (among online racks) e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30103 | 7597 | uint16 | Rack Location of Max SOC (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the highest SOC (among online racks)
| 30104 | 7598 | uint16 | Reserved | Reserved | - | - | Reserved
| 30105 | 7599 | uint16 | Rack Location of Min SOC (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the lowest SOC (among online racks)
| 30106 | 759A | uint16 | Reserved | Reserved | - | - | Reserved
| 30107 | 759B | uint16 | No. of recalibration racks | b0 ~ b15: Number of recalibration racks | ea | 1 | The number of online rack that require recalibration.
| 30108 | 759C | uint16 | Reserved | Reserved | - | - | Reserved
| 30109 | 759D | uint16 | Max SOH (among online racks) | b0 ~ b15: Max SOH | % | 0.01 | The highest (among online racks) e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30110 | 759E | uint16 | Average SOH (among online racks) | b0 ~ b15: Average SOH | % | 0.01 | The average (among online racks) e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30111 | 759F | uint16 | Min SOH (among online racks) | b0 ~ b15: Min SOH | % | 0.01 | The lowest (among online racks) e.g.) 0x20DA → 8410 * 0.01 = 84.10%
| 30112 | 75A0 | uint16 | Rack Location of Max SOH (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the highest SOH in a rack (among online racks)
| 30113 | 75A1 | uint16 | Reserved | Reserved | - | - | Reserved
| 30114 | 75A2 | uint16 | Rack Location of Min SOH (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the lowest SOH in a rack (among online racks)
| 30115 | 75A3 | uint16 | Reserved | Reserved | - | - | Reserved
| 30116 | 75A4 | uint16 | Reserved | Reserved | - | - | Reserved
| 30117 | 75A5 | uint16 | Reserved | Reserved | - | - | Reserved
| 30118 | 75A6 | uint32 | Max Cell Sum Voltage (among online racks) | b0 ~ b31: Max Cell Sum Voltage | V | 0.0001 | The highest cell sum voltage (among online racks) e.g.) 0x0072 C14D → 752058 * 0.0001 = 752.0589V
| 30119 | 75A7
| 30120 | 75A8 | uint32 | Average Cell Sum Voltage (among online racks) | b0 ~ b31: Average Cell Sum Voltage | V | 0.0001 | The average cell sum voltage (among online racks) e.g.) 0x0072 C14D → 752058 * 0.0001 = 752.0589V
| 30121 | 75A9
| 30122 | 75AA | uint32 | Min Cell Sum Voltage (among online racks) | b0 ~ b31: Min Cell Sum Voltage | V | 0.0001 | The lowest cell sum voltage (among online racks) e.g.) 0x0072 C14D → 752058 * 0.0001 = 752.0589V
| 30123 | 75AB
| 30124 | 75AC | uint16 | Rack Location of Max Cell Sum Voltage (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the highest cell sum voltage (among online racks)
| 30125 | 75AD | uint16 | Rack Location of Min Cell Sum Voltage (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the lowest cell sum voltage (among online racks)
| 30126 | 75AE | uint16 | Reserved | Reserved | - | - | Reserved
| 30127 | 75AF | uint16 | Reserved | Reserved | - | - | Reserved
| 30128 | 75B0 | sint32 | Max Current (among online racks) | b0 ~ b31: Max Current | A | 0.001 | The highest current (among online racks) e.g.) 0x0001 32A1 → 78497 * 0.001 = 78.497A, 0xFFFE CD5F → -78497 * 0.001 = -78.497A
| 30129 | 75B1
| 30130 | 75B2 | sint32 | Average Current (among online racks) | b0 ~ b31: Average Current | A | 0.001 | The average current (among online racks) e.g.) 0x0001 32A1 → 78497 * 0.001 = 78.497A, 0xFFFE CD5F → -78497 * 0.001 = -78.497A
| 30131 | 75B3
| 30132 | 75B4 | sint32 | Min Current (among online racks) | b0 ~ b31: Min Current | A | 0.001 | The lowest current (among online racks) e.g.) 0x0001 32A1 → 78497 * 0.001 = 78.497A, 0xFFFE CD5F → -78497 * 0.001 = -78.497A
| 30133 | 75B5
| 30134 | 75B6 | uint16 | Rack Location of Max Current (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the highest current (among online racks)
| 30135 | 75B7 | uint16 | Rack Location of Min Current (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the lowest current (among online racks)
| 30136 | 75B8 | uint16 | Reserved | Reserved | - | - | Reserved
| 30137 | 75B9 | uint16 | Reserved | Reserved | - | - | Reserved
| 30138 | 75BA | uint16 | Max Cell Voltage (among online racks) | b0 ~ b15: Max Cell Voltage | V | 0.001 | The highest cell voltage (among online racks) e.g.) 0xE43 → 3651 * 0.001 = 3.651V
| 30139 | 75BB | uint16 | Average Cell Voltage (among online racks) | b0 ~ b15: Average Cell Voltage | V | 0.001 | The average cell voltage (among online racks) e.g.) 0xE43 → 3651 * 0.001 = 3.651V
| 30140 | 75BC | uint16 | Min Cell Voltage (among online racks) | b0 ~ b15: Min Cell Voltage | V | 0.001 | The lowest cell voltage (among online racks) e.g.) 0xE43 → 3651 * 0.001 = 3.651V
| 30141 | 75BD | uint16 | Rack Location of Max Cell Voltage (among online racks) | b0 ~ b15 Rack ID | - | - | The rack location that has the highest cell voltage (among online racks)
| 30142 | 75BE | uint16 | Pack Location of Max Cell Voltage (among online racks) | b0 ~ b15 Pack ID | - | - | The pack location that has the highest cell voltage in a rack (among online racks)
| 30143 | 75BF | uint16 | Cell Location of Max Cell Voltage (among online racks) | b0 ~ b15: Cell ID | - | - | The cell location that has the highest cell voltage in a pack (among online racks)
| 30144 | 75C0 | uint16 | Rack Location of Min Cell Voltage (among online racks) | b0 ~ b15 Rack ID | - | - | The rack location that has the lowest cell voltage (among online racks)
| 30145 | 75C1 | uint16 | Pack Location of Min Cell Voltage (among online racks) | b0 ~ b15 Pack ID | - | - | The pack location that has the lowest cell voltage (among online racks)
| 30146 | 75C2 | uint16 | Cell Location of Min Cell Voltage (among online racks) | b0 ~ b15: Cell ID | - | - | The cell location that has the lowest cell voltage in a pack (among online racks)
| 30147 | 75C3 | uint16 | Reserved | Reserved |  |  | Reserved
| 30148 | 75C4 | uint16 | Reserved | Reserved |  |  | Reserved
| 30149 | 75C5 | sint16 | Max Pack Temperature (among online racks) | b0 ~ b15: BSC Max Pack Temperature | ℃ | 0.1 | The highest pack temperature (among online racks) e.g.) 0xAE → 175 * 0.1 = 17.5℃
| 30150 | 75C6 | sint16 | Average Pack Temperature (among online racks) | b0 ~ b15: BSC Average Pack Temperature | ℃ | 0.1 | The average pack temperature (among online racks) e.g.) 0xAE → 175 * 0.1 = 17.5℃
| 30151 | 75C7 | sint16 | Min Pack Temperature (among online racks) | b0 ~ b15: BSC Min Pack Temperature | ℃ | 0.1 | The lowest pack temperature (among online racks) e.g.) 0xAE → 175 * 0.1 = 17.5℃
| 30152 | 75C8 | uint16 | Rack Location of Max Pack Temperature (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the highest pack temperature (among online racks)
| 30153 | 75C9 | uint16 | Pack Location of Max Pack Temperature (among online racks) | b0 ~ b15: Pack ID | - | - | The pack location that has the highest pack temperature (among online racks)
| 30154 | 75CA | uint16 | Sensor Location of Max Pack Temperature (among online racks) | b0 ~ b15: Sensor ID | - | - | The sensor location that has the highest pack temperature (among online racks)
| 30155 | 75CB | uint16 | Rack Location of Min Pack Temperature (among online racks) | b0 ~ b15: Rack ID | - | - | The rack location that has the lowest pack temperature (among online racks)
| 30156 | 75CC | uint16 | Pack Location of Min Pack Temperature (among online racks) | b0 ~ b15: Pack ID | - | - | The pack location that has the lowest pack temperature (among online racks)
| 30157 | 75CD | uint16 | Sensor Location of Min Pack Temperature (among online racks) | b0 ~ b15: Sensor ID | - | - | The sensor location that has the lowest pack temperature (among online racks)
| 30158 | 75CE | uint16 | N/A |  | - | -
| 30159 | 75CF | uint16 | N/A |  | - | -
| 30160 | 75D0 | uint16 | N/A |  | - | -
| 30161 | 75D1 | uint16 | N/A |  | - | -
| 30162 | 75D2 | uint16 | N/A |  | - | -
| 30163 | 75D3 | uint16 | N/A |  | - | -
| 30164 | 75D4 | uint16 | Reserved | Reserved | - | - | Reserved
| 30165 | 75D5 | uint16 | Reserved | Reserved | - | - | Reserved
| 30166 | 75D6 | uint16 | Reserved | Reserved | - | - | Reserved
| 30167 | 75D7 | uint16 | Reserved | Reserved | - | - | Reserved
| 30168 | 75D8 | uint16 | Reserved | Reserved | - | - | Reserved
| 30169 | 75D9 | uint16 | Reserved | Reserved | - | - | Reserved

## B2C(BSC Flag)
Discrete Inputs(Modbus-TCP) Slave ID 1
The Controller must use the function code 2(0x02) to read the data.
BSC Rack Flag Data
Updated every 1 second, Read every 1 second.
Source | MODBUS Address | Name | Value | Description
Rack Flag | 1 | Rack#1 Disabled Flag Data | 0: Enabled rack, 1: Disabled rack | N Depend on Total Rack Count(Refer. B2C(BSC Data) addr. 30005)
…
| N | Rack#N Disabled Flag Data
| N+1 | Rack#1 Online Flag Data | 0: Offline rack, 1: Online rack
…
| 2N | Rack#N Online Flag Data
| 2N+1 | Rack#1 Alarm Flag Data | 0: Normal rack, 1: Alarm occurred rack
…
| 3N | Rack#N Alarm Flag Data
| 3N+1 | Rack#1 Warning Flag Data | 0: Normal rack, 1: Warning occurred rack
…
| 4N | Rack#N Warning Flag Data
| 4N+1 | Rack#1 Fault Flag Data | 0: Normal rack, 1: Fault occurred rack
…
| 5N | Rack#N Fault Flag Data
| 5N+1 | Rack#1 Non-Balancing Entry Period | 0: Normal rack, 1: Non-Balancing Entry Period occrured
…
| 6N | Rack#N Non-Balancing Entry Period

## C2B(Controller Data)
Holding Registers(Modbus-TCP) Slave ID 1
The Controller can use the function code 3(0x03) to read data and 6(0x06) or 16(0x10) to write the data.
* Click ‘Controller information’ on the BSC home screen to see the data that the controller is writing.
* 40000~40009 need to be updated every 1 second, 40010 should be updated if needed.
* BSC data check period : When the controller sends the data. (immediately)
Source | MODBUS Address | Address Hex | Type | Name | Value | Description | Unit
Controller Data | 40000 | 9C40 | uint16 | Controller Heartbeat | 0~65535 | * It is recommended to cycle from 0(zero) to 255 with an interval of 1second. * The controller’s communicating status * If this value doesn’t be changed for a long time, the BSC regards connection with the controller is broken, diagnoses the S-C LOC, and opens every rack’s contactor or disconnect switch(or circuit breaker). * The S-C LOC will be cleared as the controller sends this signal again. * The controller must diagnose the communication error and stop charging and discharging the battery section. The BSC diagnoses it and opens every rack’s contactor or disconnect switch. (or circuit breaker) | -
| 40001 | 9C41 | uint16 | Reserved |  | Reserved | -
| 40002 | 9C42 | uint16 | Reserved |  | Reserved | -
| 40003 | 9C43 | uint16 | Reserved |  | Reserved | -
| 40004 | 9C44 | uint16 | Reserved |  | Reserved | -
| 40005 | 9C45 | uint16 | Reserved |  | Reserved | -
| 40006 | 9C46 | uint16 | Reserved |  | Reserved | -
| 40007 | 9C47 | uint16 | Reserved |  | Reserved | -
| 40008 | 9C48 | uint16 | Reserved |  | Reserved | -
| 40009 | 9C49 | uint16 | Reserved |  | Reserved | -
| 40010 | 9C4A | uint16 | Command Request | 0x0000: None | Initial status | Enum
[5 empty] | 0x0001: Emergency | The command to enter Emergency mode, which means all contactors will be opened. * This command has top priority.
[5 empty] | 0x0002: Start | The command to start monitoring the battery system. The BSC connects with racks and starts monitoring the battery section. But it doesn’t act in the following situations with the ack. (Request Acknowledge 30030 : 0x5 ~ ) * If there are any racks whose state has not been changed to "Normal", the initialization will be failed due to 30 seconds timeout. * If there are any racks that you want to exclude from control, it needs disabled rack selected.(40020~40028)
[5 empty] | 0x0003: Stop | The command to stop monitoring the battery system. The BSC is disconnected from racks and stops monitoring the battery section. But it doesn’t act in the following situations with the ack. (Request Acknowledge 30030 : 0x5 ~ )
[5 empty] | 0x0004: Open All Contactors | The command to open rack’s contactor (normally all racks' contactors ) The BSC opens every rack’s contactor. But it doesn’t do in the following situations with the ack. (Request Acknowledge 30030 : 0x5 ~ )
[5 empty] | 0x0005: Close Contactors | The command to close rack’s contactor (normally all racks' contactors but not in manual mode) The BSC closes every rack’s contactor.But it doesn’t act in the following situations with the ack. (Request Acknowledge 30030 : 0x5 ~ ) * The timeout for the completion is defined as {number of target racks * 400 + 5000} (ms) * In manual mode, it needs selected rack no.(40011~40017)
[5 empty] | 0x0006: Enter Manual Mode | The command to enter manual mode The BSC enters the manual mode with opening every rack’s contactor. But it doesn’t act in the following situations with the ack. (Request Acknowledge 30030 : 0x5 ~ ) * In the manual mode, some diagnoses may not occur. Refer to the diagnostic document.
[5 empty] | 0x0007: Exit Manual Mode | The command to exit manual mode The BSC exits the manual mode and returns to the normal mode with opening every rack’s contactor. But it doesn’t act in the following situations with the ack. (Request Acknowledge 30030 : 0x5 ~ )
[5 empty] | 0x0008: | Reserved
[5 empty] | 0x0009: Event Clear | The command to clear all diagnoses * Repeated requests are not allowed within 30 seconds(Cooldown Time)
[5 empty] | 0x000A: Reset | When the reset command is executed, it clears all faults and reboots the RBMS and BSC software. * the main diagnosis, CER(Critical Error Record), requires verification with an LG Engineer and therefore is not cleared. CER : PDVF(Pack Deviation Voltage Fault), RDVF(Rack Deviation Voltage Fault)
0x000B: removed
~ Reserved
* The usage of common argument area for each command
Source | MODBUS Address | Address Hex | Type | Name | Value | Description | Unit
0x0005 Close Contactors (in Manual Mode) | 40011 | 9C4B | uint16 | Selected Rack Flags in Manual Mode | b0 ~ b15 Rack Location (1~16) | b0: Rack#1, b1: Rack#2, … b15: Rack#16 | bit flags
| 40012 | 9C4C |  |  | b0 ~ b15 Rack Location (17~32) | b0: Rack#17, b1: Rack#18, … b15: Rack#32 | bit flags
| 40013 | 9C4D |  |  | b0 ~ b15 Rack Location (33~48) | b0: Rack#33, b1: Rack#34, … b15: Rack#48 | bit flags
| 40014 | 9C4E |  |  | b0 ~ b15 Rack Location (49~64) | b0: Rack#49, b1: Rack#50, … b15: Rack#64 | bit flags
| 40015 | 9C4F |  |  | b0 ~ b15 Rack Location (65~80) | b0: Rack#65, b1: Rack#65, … b15: Rack#80 | bit flags
| 40016 | 9C50 |  |  | b0 ~ b15 Rack Location (81~96) | b0: Rack#81, b1: Rack#81, … b15: Rack#96 | bit flags
| 40017 | 9C51 |  |  | b0 ~ b15 Rack Location (97~99) | b0: Rack#97, b1: Rack#97, … b3: Rack#99, other bits are reserved | bit flags
| 40018 | 9C52 |  |  | Reserved | Reserved | bit flags
| 40019 | 9C53 |  |  | Reserved | Reserved | bit flags
Source | MODBUS Address | Address Hex | Type | Name | Value | Description | Unit
0x0002 Start | 40020 | 9C54 | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (1~16) | Disabled Rack Flags : excluded from control. b0: Rack#1, b1: Rack#2, … b15: Rack#16 | bit flags
| 40021 | 9C55 | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (17~32) | b0: Rack#17, b1: Rack#18, … b15: Rack#32 | bit flags
| 40022 | 9C56 | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (33~48) | b0: Rack#33, b1: Rack#34, … b15: Rack#48 | bit flags
| 40023 | 9C57 | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (49~64) | b0: Rack#49, b1: Rack#50, … b15: Rack#64 | bit flags
| 40024 | 9C58 | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (65~80) | b0: Rack#65, b1: Rack#66, … b15: Rack#80
| 40025 | 9C59 | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (81~96) | b0: Rack#81, b1: Rack#81, … b15: Rack#96
| 40026 | 9C5A | uint16 | Rack Flags to be disabled | b0 ~ b15 Rack Location (97~99) | b0: Rack#97, b1: Rack#97, … b3: Rack#99, other bits are reserved
| 40027 | 9C5B | uint16 | Rack Flags to be disabled | Reserved | Reserved
| 40028 | 9C5C | uint16 | Rack Flags to be disabled | Reserved | ＊These flags will be checked and applied only when BSC initializing. Please make sure to set the flags before the Start command. | bit flags

## Sequence
Accepted Example | [5 empty] | Not Accecpted Example
Emergency | [5 empty] | Emergency
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Emergency | 40010 | 0x0001 |  |  |  | Command Request: Emergency | 40010 | 0x0001
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: BMS Not Connected | 30030 | 0x0005
Last Accepted Reqeust: Emergency | 30031 | 0x0001 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC State: Emergency | 30036 | 0x0006
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Start | [5 empty] | Start
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Start | 40010 | 0x0002 |  |  |  | Command Request: Start | 40010 | 0x0002
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: BMS Already Connected | 30030 | 0x0006
Last Accepted Reqeust: Start | 30031 | 0x0002 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC State: Initializing | 30036 | 0x0002
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Stop | [5 empty] | Stop
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Stop | 40010 | 0x0003 |  |  |  | Command Request: Stop | 40010 | 0x0003
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: Current Flows | 30030 | 0x000A
Last Accepted Reqeust: Stop | 30031 | 0x0003 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC State: BMS Not Connected | 30036 | 0x0001
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Open Contactors | [5 empty] | Open Contactors
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Open Contactors | 40010 | 0x0004 |  |  |  | Command Request: Open Contactors | 40010 | 0x0004
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: All Contactors Already Opened | 30030 | 0x0008
Last Accepted Reqeust: Open Contactors | 30031 | 0x0004 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
No. of online racks: 0 | 30038 | 0
BSC SOC | 30055 | 0
BSC SOH | 30056 | 0
Etc | ~ | 0
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Close Contactors | [5 empty] | Close Contactors
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Close Contactors | 40010 | 0x0005 |  |  |  | Command Request: Close Contactors | 40010 | 0x0005
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: Over Voltage Deviation | 30030 | 0x0011
Last Accepted Reqeust: Close Contactors | 30031 | 0x0005 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
No. of online racks: > 0 | 30038 | > 0
BSC SOC | 30055 | > 0
BSC SOH | 30056 | > 0
Etc | ~ | ~
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Enter Manual | [5 empty] | Enter Manual
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Enter Manual | 40010 | 0x0006 |  |  |  | Command Request: Enter Manual | 40010 | 0x0006
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: Current Flows | 30030 | 0x000A
Last Accepted Reqeust: Enter Manual | 30031 | 0x0006 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC State: Manual | 30036 | 0x0005
No. of online racks: 0 | 30038 | 0
BSC SOC | 30055 | 0
BSC SOH | 30056 | 0
Etc | ~ | ~
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Open Contactor In Manaul Mode | [5 empty] | Open Contactor In Manual Mode
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
BSC State: Manual | 30036 | 0x0005 | [6 empty] | Command Request: Open Contactors | 40010 | 0x0004
|  |  | Command Request: Open Contactors | 40010 | 0x0004 | Request Acknowledge: All Contactors Already Opened | 30030 | 0x0008
[6 empty] | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
Request Acknowledge: In Progress | 30030 | 0x0001
Last Accepted Reqeust: Open Contactors | 30031 | 0x0004
… |  |  | Command Request: None | 40010 | 0x0000
No. of online racks: 0 | 30038 | 0
BSC SOC | 30055 | 0
BSC SOH | 30056 | 0
Etc | ~ | 0
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Close Contactor In Manual Mode | [5 empty] | Close Contactor In Manual Mode
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
BSC State: Manual | 30036 | 0x0005 | [6 empty] | Command Request: Close Contactors | 40010 | 0x0005
|  |  | Command Request: Close Contactors | 40010 | 0x0005 | Request Acknowledge: Under Contactor control | 30030 | 0x0010
|  |  | Selected Rack No in Manual Mode | 40011 | > 0 | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
|  |  |  | 40012 | > 0
|  |  |  | ~ | ~
Request Acknowledge: In Progress | 30030 | 0x0001
Last Accepted Reqeust: Close Contactors | 30031 | 0x0005
… |  |  | Command Request: None | 40010 | 0x0000
No. of online racks: > 0 | 30038 | > 0 | Selected Rack No in Manual Mode | 40011 | 0
BSC SOC | 30055 | > 0 |  | 40012 | 0
BSC SOH | 30056 | > 0 |  | ~ | ~
Etc | ~ | ~
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Exit Manual | [5 empty] | Exit Manual
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Exit Manual | 40010 | 0x0007 |  |  |  | Command Request: Exit Manual | 40010 | 0x0007
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: Current Flows | 30030 | 0x000A
Last Accepted Reqeust: Exit Manual | 30031 | 0x0007 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC State: Normal | 30036 | 0x0003
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Event Clear | [5 empty] | Event Clear
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Command Request: Event Clear | 40010 | 0x0009 |  |  |  | Command Request: Event Clear | 40010 | 0x0009
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: Within Cooldown Time | 30030 | 0x0012
Last Accepted Reqeust: Event Clear | 30031 | 0x0009 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC Information: Warning, Fault Clear | 30037 | 0x0003
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000
Start with Disabled Racks | [5 empty] | Start with Disabled Racks
BSC | Address | value | Controller | Address | value | BSC | Address | value | Controller | Address | value
|  |  | Selected Rack No excluded from control | 40020 | > 0 |  |  |  | Selected Rack No excluded from control | 40020 | > 0
|  |  |  | 40021 | > 0 |  |  |  |  | 40021 | > 0
|  |  |  | ~ | ~ |  |  |  |  | ~ | ~
|  |  | Command Request: Start | 40010 | 0x0002 |  |  |  | Command Request: Start | 40010 | 0x0002
Request Acknowledge: In Progress | 30030 | 0x0001 |  |  |  | Request Acknowledge: Target Rack Not Exist | 30030 | 0x00013
Last Accepted Reqeust: Start | 30031 | 0x0002 |  |  |  | (Other values can be set) |  |  | Command Request: None | 40010 | 0x0000
… |  |  | Command Request: None | 40010 | 0x0000
BSC State: Initializing | 30036 | 0x0002
Request Acknowledge: Done | 30030 | 0x0002
…
Request Acknowledge: None | 30030 | 0x0000
Last Accepted Reqeust | 30031 | 0x0000

## Request Ack. Table
Method / State | Not Initialized | Initializing | Normal | Normal Power Saving | Manual | Emergency
Emergency | □ "BMS Not Connected" | □ "In Progress" : BSC state will turn to Emergency. |  |  |  | □ "BSC Emergency Mode"
Start | □ "In Progress" : BSC state will turn to Initializing. | □ N/A : BSC state will turn to Normal or Not Initialized. | □ "BMS Already Connected" |  |  | □ "BMS Already Connected"
□ "Target Rack Not Exist"
Stop | □ "BMS Not Connected" |  | □ "Current Flows" : Charge status is not idle. |  |  | □ "In Progress" : BSC state will turn to Not Initialized.
□ "Under Contactor Control"
□ "In Progress" : If all of the above conditions are not met, BSC state will turn to Not Initialized.
Open All Contactors |  |  | □ "Current Flows" : Charge status is not idle. |  |  | □ "Contactors Already Opened" : The number of online racks is zero.
|  |  | □ "Contactors Already Opened" : The number of online racks is zero. |  |  | □ "In Progress" : If all of the above conditions are not met, contactors of all racks will be open.
□ "Under Contactor Control"
□ "In Progress" : If all of the above conditions are not met, contactors of all racks will be open.
Close Contactors |  |  | □ "BSC Warning or Fault" : There is section level warning/fault diagnosis. | □ "Already Online" : The number of online racks is more than zero. | □ "BSC Warning or Fault" : There is section level warning/fault diagnosis. | □ "BSC Emergency Mode"
|  |  | □ "Already Online" : The number of online racks is more than zero. |  | □ "Already Online" : The number of online racks is more than zero.
□ "Under Contactor Control"
|  |  | □ "Target Rack Not Exist" : There is no rack to close the contactor. |  | □ "Target Rack Not Exist" : The are no racks selected.
|  |  | □ "In Progress" : If all of the above conditions are not met, contactors of the racks within the range of reference voltage will be closed. |  | □ "Over Voltage(or SOC) Deviation" : The voltage(or SOC) deviation between the selected racks is too large.
□ "In Progress" : If all of the above conditions are not met, contactors of the racks within the range of reference voltage will be closed.
Enter Manual |  |  | □ "Current Flows" : Charge status is not idle. |  | □ "BSC Manual Mode"
□ "Under Contactor Control"
□ "BSC Warning or Fault" : A COF diagnosis occurs in a rack without CB.
□ "In Progress" : If all of the above conditions are not met, BSC state will turn to Manual.
Exit Manual |  |  | □ "BSC Normal Mode" | □ "BSC NPS Mode" | □ "Current Flows" : Charge status is not idle.
□ "Under Contactor Control"
□ "In Progress" : If all of the above conditions are not met, BSC state will turn to Normal.
Event Clear |  |  | □ "Within Cooldown Time" : Same request is not allowed for cooldown time(30sec) once the request has been conducted.
□ "In Progress" : If all of the above conditions are not met, all occurred diagnoses will be cleared.
Reset | □ "In Progress" : BSC will reboot itself. |  | □ "Current Flows" : Charge status is not idle. |  |  | □ "In Progress" : BSC will reboot itself.
□ "In Progress" : BSC will reboot itself.

## B2C(Rack Data)
Input Registers(Modbus-TCP) Slave ID 1
The Controller must use the function code 4(0x04) to read the data.
Rack Data
Updated every 1 second, Read every 1 second.
Rack ID : | 1 | <= Change ID to see corresponding address.
Source | MODBUS Address | Address Hex | Type | Name | Value | Unit | Scale | Description
Nameplate | 30170 | 75DA | uint32 | RBMS SW Version | b31 ~ b0: Version(x.x.x.x) | - | - | SW Version e.g.) 0x01053203 -> SW V1.5.32.3 (BCD)
| 30171 | 75DB
| 30172 | 75DC | uint32 | Updater Version | b31 ~ b0: Version(x.x.x.x) | - | - | SW Version e.g.) 0x12345678 -> SW V12.34.56.78 (BCD)
| 30173 | 75DD
| 30174 | 75DE | uint32 | Boot Selector Version | b31 ~ b0: Version(x.x.x.x) | - | - | SW Version e.g.) 0x01053203 -> SW V1.5.32.3 (BCD)
| 30175 | 75DF
| 30176 | 75E0 | uint32 | RBMS SW Checksum | b31 ~ b0: SW Checksum | - | - | e.g.) 0x01020304
| 30177 | 75E1
| 30178 | 75E2 | uint128 | BMS SW Name | b127 ~ b0: string | - | - | BMS SW Name e.g.) 0x4733585F52424D53 : "G3X_RBMS"
| 30179 | 75E3
| 30180 | 75E4
| 30181 | 75E5
| 30182 | 75E6
| 30183 | 75E7
| 30184 | 75E8
| 30185 | 75E9
| 30186 | 75EA | uint32 | BMS Serial Number | b31 ~ b0: Serial Number | - | - | Serial Number e.g.) 0x4E25F371(hex) = 1311110001(dec)
| 30187 | 75EB
| 30188 | 75EC | uint32 | BMS HW Version | b31 ~ b0: Version(x.x) | - | - | BMS HW Version e.g.) 0x00010002 -> HW V1.2 (BCD)
| 30189 | 75ED
| 30190 | 75EE | uint16 | Current Sensor Type | b15 ~ b0: Current Sensor Type | - | - | e.g.) Network Type + Hall Type : 1, Hall Type : 0
| 30191 | 75EF |  | N/A
| 30192 | 75F0 | uint16 | Relay Close Current Spec | b15 ~ b0: Current | A | 1 | Relay Close Current Spec. e.g.) 0x00C8 -> 200 A
| 30193 | 75F1 | uint16 | Pack Count | b15 ~ b0: Pack Count | ea | 1 | Pack Count e.g.) 0x0004 -> 4 (ea)
| 30194 | 75F2 | uint16 | BMIC Count per Pack | b15 ~ b0: BMIC Count | ea | 1 | BMIC Count e.g.) 0x0002 -> 2 (ea)
| 30195 | 75F3 | uint16 | Temperature Sensor Count | b15 ~ b0: Temperature Sensor Count per Pack | ea | 1 | Temperature Sensor Count per Pack e.g.) 0x0004 -> 4 (ea)
| 30196 | 75F4 |  | N/A
| 30197 | 75F5 | uint16 | PCB Temperature Sensor Count | b15 ~ b0: PCB Temperature Sensor Count per Pack | ea | 1 | Ambient Temperature Sensor Count per Pack e.g.) 0x0002 -> 2 (ea)
| 30198 | 75F6 | uint16 | Pack Voltage Sensor Count | b15 ~ b0: Pack Voltage Sensor Count per Pack | ea | 1 | Ambient Temperature Sensor Count per Pack e.g.) 0x0002 -> 2 (ea)
| 30199 | 75F7 | uint16 | Voltage Sensor Count | b15 ~ b0: Voltage Sensor Count per Pack | ea | 1 | Voltage Sensor Count per Pack e.g.) 0x000E -> 14 (ea)
| 30200 | 75F8 |  | N/A
| 30201 | 75F9 |  | N/A
| 30202 | 75FA | uint16 | Pack Type | b15 ~ b0 : Pack Type | - | - | e.g.) 0x0503
| 30203 | 75FB | uint16 | Reserved
| 30204 | 75FC | uint16 | Reserved
| 30205 | 75FD | uint16 | Reserved
| 30206 | 75FE | uint16 | Reserved
| 30207 | 75FF | uint16 | Reserved
| 30208 | 7600 | uint16 | Reserved
| 30209 | 7601 | uint16 | Reserved
| 30210 | 7602 | uint16 | Reserved
| 30211 | 7603 | uint16 | Reserved
| 30212 | 7604 | uint16 | Reserved
| 30213 | 7605 | uint16 | Reserved
| 30214 | 7606 | uint16 | Reserved
| 30215 | 7607 | uint16 | Reserved
| 30216 | 7608 | uint16 | Reserved
| 30217 | 7609 | uint16 | Reserved
| 30218 | 760A | uint16 | Reserved
| 30219 | 760B | uint16 | Reserved
Summary | 30220 | 760C | uint16 | State | 0x00 : Initialization | enum | -
0x01 : ID Set
0x02 : ID Set Complete
0x03 : BMIC Init
0x04 : Pack SOH Read Fail
0x05 : BMIC Wake Fail
0x06 : N/A
0x07 : No Configuration
0x08 : Initial Diag
0x09 : Normal
0x0A : Normal Power Saving
0x0B : Protective Power Saving
0x0C : Manual
0x0D : Emergency
: Reserved
| 30221 | 760D | uint16 | Status Flags | b15 : Reserved | big flags | -
b14~b11 : N/A
[5 empty] | b10 : Current Sensor Usage |  |  | b10 : network type : 1, hall type : 0
[5 empty] | b9 : Charge Power Control |  |  | b9 : In De-rating : 1, Not In De-rating : 0
[5 empty] | b8 : Battery Ready Status |  |  | b8 : Not Ready to Connect : 0, Ready to Connect : 1
[5 empty] | b7 : DC Line Status |  |  | b7 : Opened : 0, Closed : 1
[5 empty] | b6 ~ b5 : CER |  |  | b6 ~ b5 : Normal : 00, MDVF : 10, RDVF : 11
[5 empty] | b4 ~ b3 : Battery Charge/Discharge Status |  |  | b4 ~ b3 : Battery Idle Status : 00, Battery Discharge Status : 01, Battery Charge Status : 10
[5 empty] | b2: Fault |  |  | b2: Fault :1, No Fault :0
[5 empty] | b1: Warning |  |  | b1: Warning : 1, No Warning :0
[5 empty] | b0: Cell Balancing Status |  |  | b0: running cell balancing : 1, Not running :0
[5 empty] | Other bits reserved |  |  | Other bits reserved
| 30222 | 760E | uint16 | Component Status | b15 ~ b14 : reserved | big flags |  | b15 ~ b14 : reserved
[5 empty] | b13 ~ b12 : BPU Fan |  |  | b13 ~ b12 : No Use : 00, Use and Idle : 10, Use and Running : 11
[5 empty] | b11 ~ b10 : Pack Fan2 |  |  | b11 ~ b10 : No Use : 00, Use and Idle : 10, Use and Running : 11
[5 empty] | b9 ~ b8 : Pack Fan1 |  |  | b9 ~ b8 : No Use : 00, Use and Idle : 10, Use and Running : 11
[5 empty] | b7 ~ b6 : CB |  |  | b7 ~ b6 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b5 ~ b4 : MC(-) |  |  | b5 ~ b4 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b3 ~ b2 : MC(+) |  |  | b3 ~ b2 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b1 ~ b0 : PC |  |  | b1 ~ b0 : No Use : 00, Use and Opened : 10, Use and Closed : 11
| 30223 | 760F | uint16 | Component Feedback Status | b15 ~ b14 : Fuse | big flags |  | b15 ~ b14 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b13 ~ b12 : BPU Fan |  |  | b13 ~ b12 : No Use : 00, Use and Idle : 10, Use and Running : 11
[5 empty] | b11 ~ b10 : Pack Fan2 |  |  | b11 ~ b10 : No Use : 00, Use and Idle : 10, Use and Running : 11
[5 empty] | b9 ~ b8 : Pack Fan1 |  |  | b9 ~ b8 : No Use : 00, Use and Idle : 10, Use and Running : 11
[5 empty] | b7 ~ b6 : CB |  |  | b7 ~ b6 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b5 ~ b4 : MC(-) |  |  | b5 ~ b4 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b3 ~ b2 : MC(+) |  |  | b3 ~ b2 : No Use : 00, Use and Opened : 10, Use and Closed : 11
[5 empty] | b1 ~ b0 : reserved |  |  | b1 ~ b0 : reserved
| 30224 | 7610 | uint16 | Heart Beat (from RBMS) | heartbeat |  | - | Data is incremented by 1 (every 1sec) for a period of transmission
| 30225 | 7611 | uint16 | Live Unit Count | b15 ~ b0 : The number of wake pbms | ea | - | Awaken PBMS Count e.g.) 0x00C8 -> 200
| 30226 | 7612 | uint32 | Remaining Balancing Time | b31 ~ b0 : Remaining Balancing Time | s | 1 | e.g.) 0x00015180 -> 86400 [s]
| 30227 | 7613
| 30228 | 7614 | uint16 | SOC | b15 ~ b0 : Rack SOC | % | 0.01 | e.g.) 0x20DA -> 0x20DA / 100 = 84.10 [%]
| 30229 | 7615 | uint16 | SOH | b15 ~ b0 : Rack SOH | % | 0.01 | e.g.) 0x20DA -> 0x20DA / 100 = 84.10 [%]
| 30230 | 7616 | uint32 | Charge Power Limit | b31 ~ b0 : Charge Power Limit | kW | 0.001 | e.g.) 0x0001 1BC1 -> 0x0001 1BC1 / 1000 = 72.641 [kW]
| 30231 | 7617
| 30232 | 7618 | uint32 | Discharge Power Limit | b31 ~ b0 : Discharge Power Limit | kW | 0.001 | e.g.) 0x0001 1BC1 -> 0x0001 1BC1 / 1000 = 72.641 [kW]
| 30233 | 7619
| 30234 | 761A | uint32 | Cell Sum Voltage | b31 ~ b0 : Cell Sum Voltage | V | 0.0001 | e.g.) 0x0072 C14D -> 0x72 C14D / 10000 = 752.0589 [V]
| 30235 | 761B
| 30236 | 761C | int32 | Current | b31 ~ b0 : Current | A | 0.001 | e.g.) 0x0001 329E -> 0x0001 329E / 1000 = 78.494 [A], , 0xFFFE CD5F → -78497 / 1000 = -78.497[A]
| 30237 | 761D
| 30238 | 761E | uint16 | Rack Deviation Voltage | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Pack Deviation Voltage | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | Under Voltage | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Over Voltage | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30239 | 761F | uint16 | Rack Over Charge Current | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | N/A | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | N/A | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Sudden Voltage Drop | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30240 | 7620 | uint16 | Under Temperature | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Over Temperature | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | - | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Rack Over Discharge Current | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30241 | 7621 | uint16 | Rack Over Charge Power | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | - | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | N/A | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Deviation Temperature | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30242 | 7622 | uint16 | Under SOH | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Rack Under SOC | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | Rack Over SOC | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Rack Over Discharge Power | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30243 | 7623 | uint16 | Rack-BSC LOC by Rack | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Rack-Pack LOC | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | Frequent Balancing | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Cycle Count | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30244 | 7624 | uint16 | Reserved (for Diagnostics)
| 30245 | 7625 | uint16 | Reserved (for Diagnostics)
| 30246 | 7626 | uint16 | N/A | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Main Contactor Feedback Error | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | Temperature Sensor Error | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Current Sensor Error | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30247 | 7627 | uint16 | Contactor Open Failure | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | PBMS Fault | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | N/A | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Pack Fan Error | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30248 | 7628 | uint16 | Vaux 3.3V Error | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Vcore 1.25V Error | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | CT 13.3V Error | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | CT 5V Error | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30249 | 7629 | uint16 | N/A | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | SMPS 24V Error | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | Vpre 6.5V Error | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Vcca 5V Error | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30250 | 762A | uint16 | SBC 5V Error | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | N/A | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | MC2 24V Error | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | MC1 24V Error | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30251 | 762B | uint16 | MC Open Over Count | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | SBC Fail Safe EDC Error | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | SBC Fail Safe Redundant Error | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | SBC RSTB Error | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30252 | 762C | uint16 | - | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | - | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | - | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | RBMS Updater Version Mismatch | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30253 | 762D | uint16 | Reserved (for Diagnostics)
| 30254 | 762E | uint16 | Max Cell Voltage | b15 ~ b0 : Max Cell Voltage | V | 0.0001 | e.g.) 0x89D8 -> 0x89D8 * 0.0001 = 3.5288 [V]
| 30255 | 762F | uint16 | Min Cell Voltage | b15 ~ b0 : Min Cell Voltage | V | 0.0001 | e.g.) 0x89D8 -> 0x89D8 * 0.0001 = 3.5288 [V]
| 30256 | 7630 | uint16 | Avg Cell Voltage | b15 ~ b0 : Avg Cell Voltage | V | 0.0001 | e.g.) 0x89D8 -> 0x89D8 * 0.0001 = 3.5288 [V]
| 30257 | 7631 | uint16 | Max Cell Location | b15 ~ b8 : Pack Location | - | - | e.g.) 0x0F07 -> Pack ID : 15 / Cell ID : 7
[5 empty] | b7 ~ b0 : Cell Location | - | -
| 30258 | 7632 | uint16 | Min Cell Location | b15 ~ b8 : Pack Location | - | - | e.g.) 0x0F07 -> Pack ID : 15 / Cell ID : 7
[5 empty] | b7 ~ b0 : Cell Location | - | -
| 30259 | 7633 | int16 | Max Pack Temperature | b15 ~ b0 : Max Pack Temperature | oC | 0.1 | e.g.)0xFB -> (0xFB * 0.1) = 25.1
| 30260 | 7634 | int16 | Min Pack Temperature | b15 ~ b0 : Min Pack Temperature | oC | 0.1 | e.g.)0xFB -> (0xFB * 0.1) = 25.1
| 30261 | 7635 | int16 | Avg Pack Temperature | b15 ~ b0 : Avg Pack Temperature | oC | 0.1 | e.g.)0xFB -> (0xFB * 0.1) = 25.1
| 30262 | 7636 | uint16 | Max Temperature Location | b15 ~ b8 : Pack Location | - | - | e.g.) 0x0F07 -> Pack ID : 15 / Temperature Sensor ID : 7
[5 empty] | b7 ~ b0 : Temperature Sensor Location | - | -
| 30263 | 7637 | uint16 | Min Temperature Location | b15 ~ b8 : Pack Location | - | - | e.g.) 0x0F07 -> Pack ID : 15 / Temperature Sensor ID : 7
[5 empty] | b7 ~ b0 : Temperature Sensor Location | - | -
| 30264 | 7638 | uint16 | Max Difference of Temperature in Rack | b15 ~ b0 : Max Difference of Temperature in Rack | oC | 0.1 | e.g.)0xFB -> (0xFB * 0.1) = 25.1
| 30265 | 7639 | uint16 | Max Difference of Temperature in Pack | b15 ~ b0 : Max Difference of Temperature in Pack | oC | 0.1 | e.g.)0xFB -> (0xFB * 0.1) = 25.1
| 30266 | 763A | uint16 | removed
| 30267 | 763B | uint16 | removed
| 30268 | 763C | uint16 | removed
| 30269 | 763D | uint16 | removed
| 30270 | 763E | uint16 | MC Open Count | MC Open Count
| 30271 | 763F | uint16 | Calibration Information | b15~b8: Recalibration Count from SOX (cyclic up count: 0~9) b7~b0 : Flag for Calibration request from SOX - ex) 0x00: No request , 0x01 : SOX recommend Full Charge for SOC Recalibration
| 30272 | 7640 | uint16 | N/A
| 30273 | 7641 | uint16 | Non-balancing Entry Period | b15 ~ b0 : The elapsed time since entering the pre-condition or completing the cell balancing. | day | 1
| 30274 | 7642 | uint16 | N/A
| 30275 | 7643 | uint16 | Reserved
| 30276 | 7644 | uint16 | Reserved
| 30277 | 7645 | uint16 | Reserved
| 30278 | 7646 | uint16 | Reserved
| 30279 | 7647 | uint16 | Reserved
| 30280 | 7648 | uint16 | Reserved
| 30281 | 7649 | uint16 | Reserved
| 30282 | 764A | uint16 | Reserved
| 30283 | 764B | uint16 | Reserved
| 30284 | 764C | uint16 | Reserved
| 30285 | 764D | uint16 | Reserved
| 30286 | 764E | uint16 | Reserved
| 30287 | 764F | uint16 | Reserved
| 30288 | 7650 | uint16 | Reserved
| 30289 | 7651 | uint16 | Reserved
| 30290 | 7652 | uint16 | Reserved
| 30291 | 7653 | uint16 | Reserved
| 30292 | 7654 | uint16 | Reserved
| 30293 | 7655 | uint16 | Reserved
| 30294 | 7656 | uint16 | Reserved
| 30295 | 7657 | uint16 | Reserved
| 30296 | 7658 | uint16 | Reserved
| 30297 | 7659 | uint16 | Reserved
| 30298 | 765A | uint16 | Reserved
| 30299 | 765B | uint16 | Reserved
| 30300 | 765C | uint16 | Reserved | b15: Fault2 | - | -
b14: Fault1
b13: Warning
b12: Alarm
|  |  |  | Rack Connection Fault | b11: Fault2 | - | -
b10: Fault1
b9: Warning
b8: Alarm
|  |  |  | Current Imbalanced Fault | b7: Fault2 | - | -
b6: Fault1
b5: Warning
b4: Alarm
|  |  |  | Rack-BSC LOC by BSC | b3: Fault2 | - | -
b2: Fault1
b1: Warning
b0: Alarm
| 30301 | 765D | uint16 | Reserved (for Diagnostics by BSC)
| 30302 | 765E | uint16
| 30303 | 765F | uint16
| 30304 | 7660 | uint16
| 30305 | 7661 | uint16
| 30306 | 7662 | uint16
| 30307 | 7663 | uint16
| 30308 | 7664 | uint16
| 30309 | 7665 | uint16
| 30310 | 7666 | uint16
| 30311 | 7667 | uint16
| 30312 | 7668 | uint16
| 30313 | 7669 | uint16
| 30314 | 766A | uint16
| 30315 | 766B | uint16
| 30316 | 766C | uint16
| 30317 | 766D | uint16
| 30318 | 766E | uint16
| 30319 | 766F | uint16